## Sheet1
|  |  | Average |  | Average | DC | Average
| Load | Hours of | AC Daily | Inverter | DC Daily | System | Amp-hour
| Power (kW) | Operation | Load (kWh) | Efficiency | Load | Voltage | per day | (6 hr days)
| 50 | 6 | 300 | 0.96 | 0 | 499.2 | 626.0016
BATTERIES
| Average | (6 hr days) |  | Battery | # Batt. |  | DC |  | # Batt. | # Batt. | [7 empty] | Replace-
| Amp-hour | Days of | Discharge | Amp-hour | in |  | System | Battery | in | in | Total # | Price per | Total | Discharge | Cycle | Cycles | Life- | ment
| per day | Autonomy | Limit (DOD) | Capacity | Parallel |  | Voltage | Voltage | Series | Parallel | Batteries | Battery | Cost | Rate | Life | per Year | time | Cost/Yr
LiFePO4 | 626.0016 | 0.5 | 0.8 | 100 | 4 |  | 499.2 | 3.2 | 156 | 4 | 624 | 170.5 | 106392 | 26.6667 | 3000 | 250 | 12 | 8866 | LFP-G100 | AA Portable Power
AGM | 626.0016 | 0.5 | 0.5 | 170 | 4 |  | 499.2 | 12 | 42 | 4 | 168 | 340 | 57120 | 28.3333 | 500 | 250 | 2 | 28560 | UB4D (UPG)
ARRAY | [11 empty] | Li-ion | AGM
| Average | [5 empty] | Peak |  |  |  | 1 | 106392 | 57120
| Amp-hour | Panel | Peak Sun | Average |  | Average | Amps/ |  |  |  | 2 | 115258 | 85680
| per day | Efficiency | Hours/Day | Hours/Day |  | Peak Amps | Module |  |  |  | 3 | 124124 | 114240
| 626.0016 | 0.1512 | 6 | 690.037 |  | 100.1603 |  |  |  |  | 4 | 132990 | 142800
[11 empty] | 5 | 141856 | 171360
[11 empty] | 6 | 150722 | 199920
| Inverter Power Out |  | Batt. Cap (Ah) | Batt in Series | [6 empty] | 7 | 159588 | 228480
| 49883 |  | 100 | 102 | [6 empty] | 8 | 168454 | 257040
| Inverter Power In |  | Depth of D/C | Batt in Parallel | [6 empty] | 9 | 177320 | 285600
| 51961.4583 |  | 0.8 | 6 | [6 empty] | 10 | 186186 | 314160
| DC Current In |  | Discharge Rate (3Hr) | Total Batts | [6 empty] | 11 | 195052 | 342720
| 160 |  | 26.6667 | 612 | [6 empty] | 12 | 203918 | 371280
| DC Voltage | [9 empty] | 13 | 212784 | 399840
| 324.7591 | [9 empty] | 14 | 221650 | 428400
[11 empty] | 15 | 230516 | 456960
[11 empty] | 16 | 239382 | 485520
[11 empty] | 17 | 248248 | 514080
[11 empty] | 18 | 257114 | 542640
[11 empty] | 19 | 265980 | 571200
[11 empty] | 20 | 274846 | 599760
[11 empty] | 21 | 283712 | 628320
[11 empty] | 22 | 292578 | 656880
[11 empty] | 23 | 301444 | 685440
[11 empty] | 24 | 310310 | 714000
[11 empty] | 25 | 319176 | 742560
25
26
27
28
29
30